**Electrical air heater with controller DRH 16-5 R**

Electrical air heater for ventilation systems.

With integrated temperature controller.

With non-glowing stainless steel tubular radiators.

FR 30 P room sensor and FL 30 P channel sensor included in the scope of delivery.

Increased danger of fire if tubular radiators are dirty. Install TFE air filter as a prevention.

Recommended accessories: LW 9 air flow monitor and TFE... air filter .

Installation instructions

Mount the water-air heater on the fan's pressure side in order to prevent fan motor overheating. An arrow marked on the housing shows the default air direction through the electrical air heater.

Mount a 1 m to 1.5 m long air duct fitting between fan and electrical air heater to ensure optimum inflow to the electrical air heater.

Inflow speed can be controlled using an LW 9 air flow monitor.

If the inflow speed falls below 1.5 m/s, the electrical air heater must be switched off.

Safety instructions

Increased danger of fire if the tubular radiators are dirty. Install TFE air filter as a prevention.

Design in accordance with VDE, Device and Product Security Laws and the corresponding EU Directives.

With 2 temperature limiters switching independently of each other.

Minimum distance to inflammable material: 150 mm (if distance is less, install appropriate insulation).

Technical data

|  |  |
| --- | --- |
| Article: | DRH 16-5 R |
| Minimum air flow volume: | 110 m³/h |
| Type of voltage: | Three-phase AC |
| Rated voltage: | 400 V |
| Frequency: | 50 Hz |
| Imax: | 12,5 A |
| Degree of protection: | IP 43 |
| Mains cable: | 5 x 1,5 mm² |
| Installation: | Inside |
| Installation position: | horizontal / vertical |
| Housing material: | Sheet steel, galvanised |
| Weight: | 4,28 kg |
| Weight including packaging: | 4,68 kg |
| Nominal size: | 160 mm |
| Width: | 160 mm |
| Height: | 241 mm |
| Depth: | 375 mm |
| Width with packaging: | 235 mm |
| Height with packaging: | 305 mm |
| Depth with packaging: | 380 mm |
| Air heater type: | electrical |
| Heater power rating: | 5.000 W |
| Packing unit: | 1 piece |
| Range: | C |
| GTIN (EAN): | 4012799821434 |
| Article number: | 0082.0143 |

Manufacturer: MAICO

DRH 16-5 R Electrical air heater with controller