**Fan insert ER 100 EH**

Model with humidity control and base load circuit

Barrier-free product, as automatic switching on/off is possible via humidity control.

Fully automatic intelligent humidity control.

Switch-on humidity does not have to be set. Fan monitors the room humidity.

Automatically extracts air in full load depending on room humidity.

Not speed controllable.

Not suitable for second room air extraction.

Can be operated manually via a switch, e.g. full load is switched on using a light switch.

Standard switching: Fan runs in base load operation, humidity control is active, full load operation when the switch-on point is exceeded, base load operation when humidity falls below switch-off point.

More switching variants: Fan operation with or without base load operation; manual activation of full load; the fan is switched on/off using a switch.

Activation of full load using light switch and a fan overrun control linked to this (15 minute overrun time).

After 60 min. in humidity mode, the fan automatically switches off (or into base load) and resets the reference value for the switch-on point.

Features

Fan with cover and G2 filter (ISO Coarse > 30% class) for installation in ER-UP/GH flush-mounted housing.

For single or second room air extraction using a single fan (exception: model ER ... EH).

Trouble-free filter change without tools.

It is possible to rotate the cover by ± 5°, to compensate for housings which have been fitted at an angle.

Simple and quick installation of the fan in the housing via the snap-on attachment and the electrical plug connector.

Colour: traffic white, similar to RAL 9016.

All MAICO ER units have an IP X5 degree of protection and can be installed in area 1 in accordance with DIN VDE 0100-701, even with water jets. For details see planning instructions.

Protection class II.

The extremely steep characteristic curve shows the high pressure capacity of the ER fans.

Robust energy-saving capacitor motor.

Motor with thermal overload protection.

Maintenance-free, with enclosed ball bearings on both sides.

Volumetric flow characteristic curve and air leakage rate checked by TÜV Bayern e.V (German Technical Inspection Agency). Air leakage rate < 0.01 m³/h.

Technical data

|  |  |
| --- | --- |
| Article: | ER 100 EH |
| Model: | Humidity control |
| Air flow volume: | 35 m³/h / 100 m³/h |
| Rotating speed: | 900 1/min / 1.850 1/min |
| Air direction: | Air extraction |
| Speed controllable: |  -  |
| Type of voltage: | Alternating current |
| Rated voltage: | 230 V |
| Frequency: | 50 Hz |
| Power consumption: | 10 W / 29 W |
| Imax: | 0,09 A / 0,15 A |
| Degree of protection: | IP X5 |
| Mains cable: | 5 x 1,5 mm² |
| Installation site: | Wall / Ceiling |
| Type of installation: | Recessed-mounted |
| System type: | Decentralised |
| Material: | Synthetic material |
| Colour: | Traffic white, similar to RAL 9016 |
| Filter class: | ISO Coarse 30 % (G2) |
| Air outlet direction: | at rear |
| Airstream temperature at IMax: | 40 °C |
| Sound pressure level: | 33 dB(A) / 49 dB(A) Specifications in accordance with DIN 18017-3 at an equivalent absorption area A<sub>L</sub> = 10 m.<sup>2</sup> |
| Packing unit: | 1 piece |
| GTIN (EAN): | 4012799843849 |
| Article number: | 0084.0384 |

Manufacturer: MAICO

ER 100 EH Fan insert